## EDR Database
Cooler Frame | Baseline Capacity (ton)
| Compressor end |  |  | Drive end
| 1 pass | 2 pass | 3 pass | 1 pass | 2 pass | 3 pass
80 | 1463 | 1547 | 1548 | 1865 | 1716 | 1680
81 | 1391 | 1467 | 1468 | 1787 | 1643 | 1603
82 | 1317 | 1383 | 1384 | 1705 | 1566 | 1523
83 | N/A | N/A | 1384 | N/A | N/A | 1523
84 | 1317 | 1383 | N/A | 1705 | 1566 | N/A
85 | 1780 | 1791 | 1773 | 1957 | 1882 | 1848
86 | 1698 | 1705 | 1686 | 1869 | 1795 | 1760
87 | 1613 | 1614 | 1594 | 1778 | 1705 | 1668
88 | N/A | N/A | 1594 | N/A | N/A | 1668
89 | 1613 | 1614 | N/A | 1778 | 1705 | N/A
8K | N/A | N/A | 1685 | N/A | N/A | 1744
8L | N/A | N/A | 1620 | N/A | N/A | 1715
8M | N/A | N/A | 1552 | N/A | N/A | 1674
8P | 1595 | 1689 | N/A | 1889 | 1761 | N/A
8Q | 1533 | 1624 | N/A | 1865 | 1735 | N/A
8R | 1468 | 1555 | N/A | 1800 | 1725 | N/A
8T | N/A | N/A | 1909 | N/A | N/A | 1934
8U | N/A | N/A | 1837 | N/A | N/A | 1900
8V | N/A | N/A | 1762 | N/A | N/A | 1822
8X | 1896 | 1922 | N/A | 2015 | 1952 | N/A
8Y | 1828 | 1850 | N/A | 1983 | 1920 | N/A
8Z | 1756 | 1775 | N/A | 1909 | 1845 | N/A
Cooler Length | Compressor End Water Entering |  |  | Drive End Water Entering
| A1 | A2 | A3 | A1 | A2 | A3
14 ft | 2.2688e-05 | -0.0017183 | 1.0146 | -6.1431e-05 | 0.0086862 | 0.91986
16 ft | -3.7504e-05 | 0.003987 | 0.96392 | -8.7204e-05 | 0.0082889 | 0.92563
Cooler Length |  | 14 ft | 16 ft
Compressor End | A1 | 2.2688e-05 | -3.7504e-05
| A2 | -0.0017183 | 0.003987
| A3 | 1.0146 | 0.96392
Drive End | A1 | -6.1431e-05 | -8.7204e-05
| A2 | 0.0086862 | 0.0082889
| A3 | 0.91986 | 0.92563
| C1 | C2 | C3
Compressor End | 8.0163e-05 | 0.0096884 | 0.4985
Drive End | 7.092e-05 | 0.0097842 | 0.50737
| Compressor End | Drive End
C1 | 8.0163e-05 | 7.092e-05
C2 | 0.0096884 | 0.0097842
C3 | 0.4985 | 0.50737
| 19XRF | 19XR6
Vapor Limit(EDR) | #NAME? | #REF!
Liquid Limit(ETO) | #NAME? | #REF!
| 19XRF | 19XR6
Economizer Vapor Volume Flow Rate | #NAME? | #REF!
V_EyeHole.Liquid m1st | #NAME? | #REF!
| Pass | Failed
D With Baffle | 采用D with baffle 经济器，ETO选型通过，但有风险，首台应用需要测试。 | 选型未通过
0 | 选型通过，机组布置需重新设计，外型尺寸/重量等需更新。 | 选型未通过

## 19XRF_Evap (hidden)
Input_E-cat report
Case Name
| Chiller Capacity | Ton | 1928
| Cooler Size |  | 89
| Cooler Passes |  | 2
| Cooler Nozzle Arrangement |  | Drive end
| Cooler Entering Temperature | F | 70
| Cooler Saturation Temperature(Tsat,clr) | F | 56.8
| Cooler Leaving Temperature | F | 57.2
| Economizer Saturation Temperature(Tsat,eco) | F | 77.77
Output_Cooler Limit Tons
| Baseline Capacity |  | 1705
| C1 |  | 7.092e-05
| C2 |  | 0.0097842
| C3 |  | 0.50737
| Lift Multiplier |  | 1.2919
| Rise Multiplier |  | 1
| Lift*Rise |  | 1.2919
| Cooler Limit Tons | Ton | 2202.7154
Compressor end |  |  | D With Baffle
Drive end
1
2
3
80 | 16
81
82
83
84
8K
8L
8M
8P
8Q
8R
14
16

## 19XRF_Econ (hidden)
18inch Economizer
PARAMETER |  | Cooler:14/20 Condenser: 32/37 | LL_1850TR_20143237 | LL_1920TR_20143237_14C32C6752KW | LL_1950TR_20143237_14C32C6892KW | LL_1990TR_20143237_14C32C7033KW | LL_2022TR_20143237_14C32C7033KW B | LL_2020TR_20143237_14C32C7104KW | Asia Max capacity 256.5Kpag_872Kpag | Asia_Max Capacity_IGV93.6%_257Kpag_872Kpag | 1500RT_Asia100%_257Kpag_872.5Kpag | 1500RT_Asia100%_257Kpag_872.5Kpag B | Asia KPI 1140KG_257.5Kpag_885Kpag
INPUT
Refrigerant |  | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a
Capacity | tons | 1928 | 1849.5978 | 1920.0108 | 1950.0553 | 1989.7599 | 2022.3507 | 2015.5025 | 1508.0332 | 1544.3798 | 1502.4794 | 1511.5955 | 1817.8089
Flasc SaturationTemperature | F | 96.52 | 95.7981 | 95.8685 | 96.1201 | 96.3162 | 96.4805 | 96.2893 | 96.2429 | 96.1559 | 95.8479 | 95.807 | 96.0976
Economizer Saturation Temperature | F | 77.77 | 77.3 | 78.5075 | 79.083 | 79.7756 | 80.2474 | 81.2772 | 71.3823 | 71.5644 | 71.5536 | 71.4768 | 73.3346
Cooler Saturation Temperature | F | 56.8 | 53.705 | 53.6598 | 53.5205 | 53.4984 | 52.9153 | 53.3095 | 42.0136 | 42.1312 | 42.3269 | 42.2286 | 42.27
Condenser Saturation Temperature | F | 100.1 | 102.0164 | 102.0888 | 102.3763 | 102.5663 | 102.7422 | 103.2538 | 101.1484 | 101.1699 | 100.9976 | 100.9801 | 102.1913
Discharge Super Heat | R | 13 | 11.34 | 11.52 | 11.7 | 11.88 | 12.6 | 12.42 | 12.3049 | 13.0427 | 12.956 | 12.9511 | 10.113
Evaporator LTD | R | 0.4 | 3.5988 | 3.7206 | 3.7654 | 3.8073 | 4.408 | 3.9359 | 3.0425 | 2.9059 | 2.9788 | 2.9636 | 3.3841
System Lift | R | 43.3 | 48.3114 | 48.429 | 48.8558 | 49.0678 | 49.827 | 49.9443 | 59.1348 | 59.0387 | 58.6707 | 58.7515 | 59.9213
Constant
Acceleration of Gravity | ft/sec^2 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174 | 32.174
OUTPUT
Cooler Saturation vapor Enthalpy h | Btu/lbm | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Cooler SaturationLiquid Enthalpy h | Btu/lbm | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Flasc Saturation Liquid Enthalpy h5 | Btu/lbm | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Saturation Liquid Enthalpy h6 | Btu/lbm | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Saturation Vapor Enthalpy h7 | Btu/lbm | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Vapor quality |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Refrigerator Dryness |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Saturation Liquid Density | lbm/ft^3 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Saturation Vapor Density | lbm/ft^3 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Mixture Density | lbm/ft^3 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
1st stage Mass Flow Rate | lb/min | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Econ Vapor Mass Flow Rate | lb/min | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Econ Liquid Mass Flow Rate | lb/min | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Vapor Volume Flow Rate | ft^3/min | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Economizer Liquid Volume Flow Rate | ft^3/min | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Assume
Shell ID | in | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126 | 17.2126
Shell Length | in | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
d_ 2nd stg Vapor | in | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
d_ Econ. Liquid | in | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
A_EyeHole | ft^2 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71
Calculation
A_Econ Shell_V | ft^2 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159 | 1.6159
A_Econ Shell_H | ft^2 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696 | 7.7696
A_ 2nd stg Vapor | ft^2 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635
A_ Econ. Liquid | ft^2 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635 | 0.13635
Check
V_ 2nd stg Vapor | ft/s | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
V_ Econ. Liquid | ft/s | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
V_EyeHole.Liquid m1st | ft/s | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
V_Liquid_Econ_H | ft/s | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
V_Vapor_Econ_H | ft/s | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
V_Vapor_Econ_V | ft/s | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
ρv^2 (Vapor)<*** |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
|  |  | 3.5988 | 3.7206 | 3.7654 | 3.8073 | 4.408 | 3.9359 | 3.0425 | 2.9059 | 2.9788 | 2.9636 | 3.3841
Lliquid carry over | %
Vapor Limit(EDR) | ft^3/min | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Liquid Limit(ETO) | ft/s | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
|  |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?

## 19XRF Low Lift Eco&Cooler Check
PARAMETER |  | Cooler:14/20 Condenser: 32/37
INPUT |  |  | 注释 | 此Tool仅应用于19XRF数据中心中温工况ETO订单中，Igonre Carryover的选型进行校核。采用XRF ETO经济器的订单必须进行5天性能测试。
Refrigerant |  | R134a |  | Comments:
Chiller Capacity | tons | 1928 | #此值根据E-Cat报告进行输入 |  | 该区域值来自E-Cat报告（Ignore LCO)
Cooler Size |  | 89 | #此值根据E-Cat报告进行选择 | D With Baffle | 带Suction Baffle的19XRF 经济器浮球阀代号
Cooler Passes |  | 2 | #此值根据E-Cat报告进行选择 | OK | E-Cat 选型符合EDR的限制
Cooler Nozzle Arrangement |  | Drive end | #此值根据E-Cat报告进行选择 | NO | E-Cat 选型不符合EDR的限制
Cooler Entering Temperature | F | 70 | #此值根据E-Cat报告进行输入 | Pass | E-Cat 选型工况同时满足EDR中经济器和蒸发器的限制
Cooler Saturation Temperature(Tsat,clr) | F | 56.8 | #此值根据E-Cat报告进行输入 | Failed | E-Cat 选型工况不满足EDR中经济器和蒸发器的限制中的任一项
Cooler Leaving Temperature | F | 57.2 | #此值根据E-Cat报告进行输入
Condenser Saturation Temperature | F | 100.1 | #此值根据E-Cat报告进行输入
Flasc SaturationTemperature | F | 96.52 | #此值根据E-Cat报告进行输入
ETO Economizer Float Valve Size |  | D With Baffle | #此值根据ETO选型进行选择,代号含义见Comments
Economizer Saturation Temperature(Tsat,eco) | F | 77.77 | #此值根据E-Cat报告进行输入
Discharge Super Heat | R | 13 | #此值根据E-Cat报告进行输入
Evaporator LTD | R | 0.4 | #此值根据E-Cat报告进行输入
Limit
Vapor Limit(EDR) | ft^3/min | #NAME? | #EDR中经济器气体体积流量限制值 |  | 1
Liquid Limit(ETO) | ft/s | #NAME? | #EDR中经济器眼睛口液体流速限制值
Cooler Limit Tons | tons | 2202.7154
Check
Economizer Vapor Volume Flow Rate | ft^3/min | #NAME? | #E-Cat选型中，经济器气体体积流量
V_EyeHole.Liquid m1st | ft/s | #NAME? | #E-Cat选型中，经济器眼睛口液体流速
Economizer Vapor Volume Flow Rate | ft^3/min | #NAME? | #判断E-Cat选型中经济器的气体体积流量是否满足EDR限制
V_EyeHole.Liquid m1st | ft/s | #NAME? | #判断E-Cat选型中经济器的液体流速是否满足EDR限制
Cooler Limit check | tons | OK | #判断E-Cat选型中蒸发器的Limit Tons是否满足EDR限制
Result |  | #NAME? | #判断E-Cat选型中经济器和蒸发器的Limit Tons是否均满足EDR限制
结论: |  | #NAME?

## XRF LL Test Data (hidden)
| 孔板F32 | 孔板F32 | 孔板F32 | 孔板F32 | 孔板F32 | 孔板F36 | 14th | 14th | 14th | 14th
Date: | 2021-01-28 | 2021-01-28 | 2021-01-28 | 2021-01-28 | 2021-01-28 | 2021-02-01 | 2020-06-05 | 2020-07-04 | 2020-07-06 | 2020-07-06 | 2020-04-22
Time | 19:50 | 20:55 | 21:46 | 22:14 | 22:51 | 11:09 | 12:24 | 9:03 | 9:01 | 10:22 | 17:57
Compressor Code | F30 | F30 | F30 | F30 | F30 | F30 | F30 | F30 | F30 | F30 | F50
Gear Code | T | T | T | T | T | T | T | T | T | T | T
Drive | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing | VFD - Free standing
Economizer | w/ | w/ | w/ | w/ | w/ | w/ | w/ | w/ | w/ | w/ | w/
Test Item | LL_1850TR_20143237 | LL_1920TR_20143237_14C32C6752KW | LL_1950TR_20143237_14C32C6892KW | LL_1990TR_20143237_14C32C7033KW | LL_2022TR_20143237_14C32C7033KW B | LL_2020TR_20143237_14C32C7104KW | Asia Max capacity 256.5Kpag_872Kpag | Asia_Max Capacity_IGV93.6%_257Kpag_872Kpag | 1500RT_Asia100%_257Kpag_872.5Kpag | 1500RT_Asia100%_257Kpag_872.5Kpag B | Asia KPI 1140KG_257.5Kpag_885Kpag
Test ID | 2 | 3 | 4 | 5 | 6 | 8 |  | 1 | 气源控制阀强制启用 气源控制阀强制值关闭 | 气源控制阀强制启用 气源控制阀强制值打开 | T13_014
Test Frequency | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2
ITEM
Comments | [6 empty] | 14th | 14th |  |  | VS球阀打开 气源控制阀强制停用 气源控制阀强制值关闭
Chiller
Refrigerant Charge Amount | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275 | 2513.2275
Atmospheric pressure | 14.5109 | 14.5109 | 14.5109 | 14.5109 | 14.5109 | 14.5109 | 14.5762 | 14.5472 | 14.4892 | 14.4892 | 14.7938
Chiller Power Factor | 0.90887 | 0.9097 | 0.90982 | 0.90958 | 0.90849 | 0.91021 | 0.9051 | 0.90219 | Power Meter Mistake | 0.90318 | 0.90826
System | 41.5479 | 41.3208 | 41.5826 | 41.6847 | 41.7521 | 42.1478 | 5303.4511 | 5431.2748 | 5283.9194 | 5315.9792 | 6392.8704
Chiller Cooling Capacity | 1849.5978 | 1920.0108 | 1950.0553 | 1989.7599 | 2022.3507 | 2015.5025 | 1508.0332 | 1544.3798 | 1502.4794 | 1511.5955 | 1817.8089
Input Power | 967.86 | 1013.4877 | 1037.2985 | 1064.8708 | 1089.2354 | 1115.8708 | 918.8895 | 938.7189 | 912.5465 | 914.4564 | 1126.7864
Heat Rejection | 7514.2777 | 7871.149 | 7986.163 | 8123.4339 | 8279.5728 | 8253.7242 | 6319.1381 | 6407.0883 | 6228.4685 | 6256.3118 | 7568.7208
Chiller Performance | 0.52328 | 0.52786 | 0.53193 | 0.53518 | 0.5386 | 0.55364 | 0.60933 | 0.60783 | 0.60736 | 0.60496 | 0.61986
COP | 6.7207 | 6.6624 | 6.6114 | 6.5713 | 6.5295 | 6.3521 | 5.7716 | 5.7858 | 5.7903 | 5.8133 | 5.6735
Heat Balance | -0.5556% | -1.339% | -1.138% | -0.7506% | -0.9437% | -0.6026% | -1.532% | -0.579% | -0.5138% | -0.4136% | -0.6482%
System Lift | 48.3114 | 48.429 | 48.8558 | 49.0678 | 49.827 | 49.9443 | 59.1348 | 59.0387 | 58.6707 | 58.7515 | 59.9213
Compressor
IGV Opening | 52% | 62.5% | 68.5% | 80% | 90% | 93.6% | 93.6% | 93.6% | 91% | 91% | 93.6%
Suct. Pipe Temp. 1 | 53.4121 | 53.2641 | 53.0504 | 52.9784 | 52.2575 | 52.6806 | 40.5928 | 40.2993 | 40.6366 | 40.504 | 39.704
Suct. Pipe Temp. 2 | 52.6949 | 52.4864 | 52.2737 | 52.183 | 51.5376 | 51.8511 | #N/A | #N/A | #N/A | #N/A | #N/A
Suct. Pipe Temp. 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 41.6731 | 41.7875 | 42.0293 | 41.9897 | 41.4085
Suct. Pipe Temp. 4 | 53.5335 | 53.4664 | 53.2694 | 53.2368 | 52.4879 | 52.9948 | #N/A | #N/A | #N/A | #N/A | #N/A
Suct. Pipe Temp. 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Suct. Pipe Temp. 6 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Suct. Pipe Static Press. 1 | 63.1866 | 63.0662 | 62.8032 | 62.7173 | 62.0445 | 61.9829 | #N/A | #N/A | #N/A | #N/A | #N/A
Suct. Pipe Static Press. 2 | 63.5357 | 63.4543 | 63.2542 | 63.1763 | 62.4421 | 62.3356 | 49.7696 | 50.4772 | 50.6686 | 50.5672 | 50.0762
Suct. Pipe Static Press. 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -76.4414 | -76.4704 | -76.5283 | -76.5283 | -75.6001
Suct. Pipe Static Press. 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 51.0701 | 51.2231 | 51.3369 | 51.2237 | 51.5024
Suct. Pipe Static Press. 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Suct. Pipe Static Press. 6 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Suct. Pipe Total Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Suction Pressure Drop | 1.0414 | 1.0855 | 1.1633 | 1.1984 | 1.22 | 1.8479 | 1.9445 | 1.3538 | 1.3577 | 1.361 | 1.8932
Suction Superheat | 0.21839 | 0.12712 | 0.11398 | 0.10351 | 0.031831 | 0.4735 | 0.56365 | -0.4589 | -0.31729 | -0.3462 | -0.64208
Comp Volute Disch. Temp.1 | 112.9868 | 113.4644 | 113.7442 | 114.0333 | 115.0347 | 115.0002 | 112.9065 | 113.2925 | 112.8783 | 112.8593 | 112.3223
Comp Volute Disch. Temp.2 | 114.7478 | 114.9851 | 115.4653 | 115.961 | 116.8902 | 117.0881 | 1.7831e+38 | 1.7831e+38 | 1.7831e+38 | 1.7831e+38 | 1.7831e+38
Comp Volute Disch. Static Press. 1 | 143.7639 | 143.8821 | 144.502 | 145.0792 | 145.5169 | 146.2109 | 140.9952 | 140.6874 | 139.8756 | 139.8012 | 142.9275
Comp Volute Disch. Static Press. 2 | 143.0467 | 143.2814 | 143.8431 | 144.4158 | 144.5917 | 145.5182 | 141.3527 | 139.1549 | 138.3867 | 138.3412 | 143.1647
Discharge Pressure Drop | 0.2704 | 0.29138 | 0.26302 | 0.42768 | 0.35369 | 0.052704 | 0.094299 | -1.1923 | -1.4432 | -1.4762 | -0.22595
Discharge Superheat | 11.34 | 11.52 | 11.7 | 11.88 | 12.6 | 12.42 | 12.3049 | 13.0427 | 12.956 | 12.9511 | 10.113
Comp Suct. Housing Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Comp Volute Disch. Total Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Comp Volute Static Press. 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 137.3146 | 137.6661 | 136.9758 | 136.8767 | 140.1836
Comp Volute Static Press. 2 | 1.4303e+37 | 1.3202e+37 | 9.9017e+36 | 1.4303e+37 | 1.4303e+37 | 1.4303e+37 | 1.4365e+37 | 1.4365e+37 | 1.4365e+37 | 1.4365e+37 | 8.4883e+36
Comp Volute Static Press. 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Interstage Suction Press. 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 86.0975 | 86.3217 | 86.3146 | 86.1874 | 88.397
Interstage Suction Press. 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 89.1742
Interstage suction temp. 1 | 77.3439 | 78.7054 | 79.2834 | 79.7896 | 80.4959 | 81.2276 | 71.6572 | 72.5285 | 72.4848 | 72.4275 | 71.7221
Interstage suction temp. 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Disch. Pipe Ent. Static Press. 1 | -75.7998 | -75.8004 | -75.798 | -75.7948 | -75.7985 | -75.7994 | 140.4341 | 140.2351 | 139.6134 | 139.5115 | 142.6683
Disch. Pipe Ent. Static Press. 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 141.4329 | 140.9575 | 140.6127 | 140.5074 | 143.4175
Disch. Pipe Ent. Temp. 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.851e+38 | 1.851e+38 | 1.851e+38 | 1.851e+38 | 1.0938e+38
Disch. Pipe Ent. Temp. 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7848e+38 | 1.7848e+38 | 1.7848e+38 | 1.7848e+38 | 1.7848e+38
Disch. Pipe Exit Static Press. 1 | 143.845 | 144.0905 | 144.7004 | 145.2445 | 145.5334 | 146.4764 | #N/A | #N/A | #N/A | #N/A | #N/A
Disch. Pipe Exit Static Press. 2 | -75.8446 | -75.8433 | -75.8431 | -75.8435 | -75.8436 | 146.5844 | #N/A | #N/A | #N/A | #N/A | #N/A
Disch. Pipe Exit Temp. 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7812e+38 | 1.7812e+38 | 1.6641e+38 | 1.7812e+38 | 1.7812e+38
Disch. Pipe Exit Temp. 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 113.9013 | 113.8071 | 113.2982 | 113.2506 | 111.8538
Disch. Pipe Exit Temp. 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Disch. Isolation Valve Ent. Static Press. | 34.0002 | 34.1236 | 34.4287 | 34.7005 | 34.8449 | 146.5304 | #N/A | #N/A | #N/A | #N/A | #N/A
Disch. Isolation Valve Exit Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Discharge Pressure Drop_Isolation Valve | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Comp Oil Tank Oil Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
Evaporator
Cooler Entering Temp. | 68.132 | 68.1901 | 68.2829 | 68.5015 | 68.6927 | 68.6286 | 54.1093 | 54.3225 | 54.3382 | 54.275 | 54.7798
| 20.0733 | 20.1056 | 20.1572 | 20.2786 | 20.3848 | 20.3492 | 12.283 | 12.4014 | 12.4101 | 12.375 | 12.6555
Cooler Leaving Temp. | 57.3038 | 57.3804 | 57.2858 | 57.3058 | 57.3232 | 57.2454 | 45.0561 | 45.0371 | 45.3057 | 45.1922 | 45.6541
| 14.0577 | 14.1002 | 14.0477 | 14.0588 | 14.0685 | 14.0252 | 7.2534 | 7.2428 | 7.3921 | 7.329 | 7.5856
Evap. TPILE | 10.8281 | 10.8097 | 10.997 | 11.1957 | 11.3695 | 11.3832 | 9.0532 | 9.2854 | 9.0325 | 9.0828 | 9.1258
Cooler Flow Rate | 4095.5955 | 4258.8178 | 4251.7735 | 4261.4606 | 4265.159 | 4245.5315 | 3981.3723 | 3975.4832 | 3976.086 | 3977.9426 | 4761.8716
Cooler Pressure Drop | 20.0152 | 21.692 | 21.6832 | 21.7389 | 21.8573 | 21.656 | 26.7681 | 24.8328 | 25.142 | 25.206 | 32.4487
Evap. Shell Static Press. | 64.4025 | 64.3457 | 64.1919 | 64.1452 | 63.4633 | 64.0072 | 51.714 | 51.8311 | 52.0262 | 51.9282 | 51.9694
Evap. Shell Static Press. Motor End | 64.3518 | 64.3023 | 64.1292 | 64.1243 | 63.4449 | 63.8201 | 51.8177 | 51.8712 | 51.8978 | 51.9283 | 52.1302
Evaporator Saturation Temp. | 53.705 | 53.6598 | 53.5205 | 53.4984 | 52.9153 | 53.3095 | 42.0136 | 42.1312 | 42.3269 | 42.2286 | 42.27
Evaporator LTD | 3.5988 | 3.7206 | 3.7654 | 3.8073 | 4.408 | 3.9359 | 3.0425 | 2.9059 | 2.9788 | 2.9636 | 3.3841
Condenser | 23.0822 | 22.956 | 23.1015 | 23.1582 | 23.1956 | 23.4155
Condenser Entering Temp. | 89.7596 | 89.5381 | 89.5593 | 89.513 | 89.4416 | 89.7765 | 89.8926 | 89.4197 | 89.4046 | 89.3341 | 90.0993
| 32.0887 | 31.9656 | 31.9774 | 31.9517 | 31.912 | 32.0981 | 32.1626 | 31.8998 | 31.8914 | 31.8523 | 32.2774
Condenser Leaving Temp. | 98.8517 | 98.7012 | 98.8685 | 98.9905 | 99.0753 | 99.3932 | 99.0752 | 98.7294 | 98.4573 | 98.4172 | 99.2869
| 37.1398 | 37.0562 | 37.1492 | 37.2169 | 37.2641 | 37.4407 | 37.264 | 37.0719 | 36.9207 | 36.8985 | 37.3816
Cond. TPILE | 9.0921 | 9.1631 | 9.3092 | 9.4774 | 9.6337 | 9.6167 | 9.1825 | 9.3097 | 9.0527 | 9.0832 | 9.1876
Condenser Flow Rate | 5670.4942 | 5893.5397 | 5885.9349 | 5880.8743 | 5896.6563 | 5889.0356 | 4721.7891 | 4721.7397 | 4720.2646 | 4725.4228 | 5652.6211
Condenser Pressure Drop | 58.3299 | 62.1952 | 62.2183 | 62.3052 | 62.6535 | 64.5058 | 27.5381 | 33.0454 | 33.14 | 33.2851 | 36.3471
Cond. Shell Static Press. | 143.2206 | 143.4147 | 143.9894 | 144.4516 | 144.8303 | 145.987 | 141.279 | 141.3249 | 140.9583 | 140.9214 | 143.5109
Cond. Shell Static Press. Motor End | 143.0491 | 143.166 | 143.8297 | 144.1881 | 144.571 | 145.6366 | 140.8802 | 140.9021 | 140.1904 | 140.1733 | 143.0332
Condenser Saturation Temp. | 102.0164 | 102.0888 | 102.3763 | 102.5663 | 102.7422 | 103.2538 | 101.1484 | 101.1699 | 100.9976 | 100.9801 | 102.1913
Condenser LTD | 3.1647 | 3.3876 | 3.5078 | 3.5758 | 3.6669 | 3.8605 | 2.0732 | 2.4405 | 2.5403 | 2.5629 | 2.9043
Flasc Exit Static Press. | 130.2358 | 130.3766 | 130.8814 | 131.2758 | 131.6068 | 131.2216 | 131.1282 | 130.9534 | 130.3353 | 130.2535 | 130.8362
Flasc Saturation Temp. | 95.7981 | 95.8685 | 96.1201 | 96.3162 | 96.4805 | 96.2893 | 96.2429 | 96.1559 | 95.8479 | 95.807 | 96.0976
Flasc Exit Temp. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 95.9555 | 95.8452 | 95.5603 | 95.5437 | 95.5715
ΔP though Flasc Orifice | 12.8991 | 12.9138 | 13.0281 | 13.044 | 13.0938 | 14.5903 | 10.1508 | 10.3715 | 10.623 | 10.6679 | 12.6747
FLASC Subcooling | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.28738 | 0.31072 | 0.28754 | 0.26325 | 0.52613
Sump Exit Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Sump Exit Temp. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Economizer | 95.9928 | 96.0053 | 96.0901 | 96.2077 | 95.822 | 96.5368 | 85.4582 | 85.5388 | 85.4665 | 85.4305 | 86.3556
Liquid level in Economizer SG5 | SG 8 1/4 | SG 8 1/4 | SG 8 1/4 |  | SG 8 1/4 | SG 7 1/2 | #N/A | #N/A | #N/A | #N/A | #N/A
Liquid level in low side float chamber | SG 3_half | SG 3_half | SG 3_half |  | SG 3_half | SG 4 | SG 4 | SG 4 | SG 4 | SG 4 | SG 4
Econ. Shell Static Press. | 96.9853 | 98.9359 | 99.8758 | 101.0159 | 101.7981 | 103.5214 | 87.8428 | 88.114 | 88.0979 | 87.9835 | 90.7837
Economizer Saturation Temp. | 77.3 | 78.5075 | 79.083 | 79.7756 | 80.2474 | 81.2772 | 71.3823 | 71.5644 | 71.5536 | 71.4768 | 73.3346
Float Ball Valve Housing Static Press. | -58.5404 | -58.5422 | -58.541 | -58.5402 | -58.5403 | -58.5404 | 65.6888 | -58.5042 | -58.5621 | -58.5621 | 60.5684
Liquid Piping
Condenser outlet ball valve open / close | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open
Fix orifice outlet ball valve open / close | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open
Cooler inlet butterfly valve opening | Fully Open | Fully Open | Fully Open | Fully Open | Fully Open | Fully Open | Fully Open | Fully Open | Fully Open | Fully Open | Fully Open
Liquid level @ sump | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble | Full W/o bubble
Liquid level switch @ sump | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Liquid line (Aero test) butterfly valve opening | Totally Close | Totally Close | Totally Close | Totally Close | Totally Close | Totally Close | Totally Close | Totally Close | Totally Close | Totally Close | Totally Close
Liquid line (Aero test) EXV opening | 关 | 关 | 关 | 关 | 关 | 关 | 关 | 关 | 关 | 关 | 关
Orifice Ent. Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 127.7036 | 127.3581 | 126.8663 | 129.5974 | 126.0237
Orifice Exit Static Press. | -58.0511 | -58.0521 | -58.051 | -58.0512 | -58.0514 | -58.0515 | -57.9862 | -58.0152 | -58.0731 | -58.0731 | -57.7686
Econ. Ent. Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Bypass EXV Exit Static Press. | - | - | - | - | - | - | - | - | - | - | -
Float Ball Valve Housing Exit Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.491 | -73.418 | -73.4757 | -73.4756 | 90.6592
Evap. Ent. Static Press. | -73.2243 | -73.2255 | -73.2253 | -73.225 | -73.2246 | -73.2244 | 58.7905 | -73.1882 | -73.2461 | -73.2462 | 62.0615
ΔP Sump - Orifice | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.4246 | 3.5953 | 3.469 | 0.65602 | 4.8125
ΔP Orifice | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 185.6898 | 185.3733 | 184.9394 | 187.6705 | 183.7923
ΔP Econ Inlet - Econ shell | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ΔP High side liquid line | 33.2505 | 31.4407 | 31.0056 | 30.2599 | 29.8087 | 27.7002 | 43.2854 | 42.8393 | 42.2374 | 42.27 | 40.0526
ΔP Float ball | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.6482 | 161.532 | 161.5736 | 161.4591 | 0.12443
ΔP Float valve - Evap | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.7005 | -0.22978 | -0.22956 | -0.22947 | 28.5978
ΔP distributor | -137.6268 | -137.5712 | -137.4173 | -137.3701 | -136.6878 | -137.2316 | 7.0765 | -125.0193 | -125.2723 | -125.1743 | 10.0921
Vapor Piping
Vapor source line ball valve open / close | Close | Close | Close | Close | Close | Close | Close | Close | Close | Close | Close
Vapor source line solenoid valve open / close | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open
2nd stg suction line butterfly valve open / close | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open
Damper Valve Ent. Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Damper Valve Exit Static Press. | -76.3336 | -76.3378 | -76.3335 | -76.3332 | -76.3327 | -76.3334 | -76.2682 | -76.2971 | -76.355 | -76.3551 | -76.0506
2nd stage Suct. Pipe Static Press. | 95.5656 | 97.632 | 98.7148 | 99.8968 | 100.8054 | 102.3625 | 86.051 | 86.3345 | 86.1877 | 86.0913 | 88.1656
2nd stage Suct. Pipe Temp. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 70.1059 | 70.0582 | 69.9882 | 69.9164 | 71.0595
ΔP Damper | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Superheat after Damper Valve | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -0.062463 | -0.30358 | -0.27347 | -0.27955 | -0.53941
ΔP Economizer - 2nd Suction | 1.4197 | 1.3038 | 1.161 | 1.1191 | 0.99268 | 1.1588 | 1.7918 | 1.7795 | 1.9102 | 1.8922 | 2.6181
HGBP Pressure
HGBP opening_Motor End | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
HGBP Ent. Static Press. Motor End | - | - | - | - | - | - | - | - | - | - | -
HGBP Exit Static Press. Motor End | - | - | - | - | - | - | - | - | - | - | -
ΔP HGBP_Motor End | - | - | - | - | - | - | - | - | - | - | -
HGBP opening_cmpr end | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
HGBP Ent. Static Press. Cmpr End | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
HGBP Exit Static Press. Cmpr End | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ΔP HGBP_Cmpr End | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Motor & Oil Lubrication
Motor housing Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 59.3358 | 59.5533 | 59.6053 | 59.4281 | #N/A
Motor Cooling Liquid Supply Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 139.8333 | #N/A | #N/A | #N/A | 133.3191
Motor Housing Liquid Drain Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Motor Winding Temp. | 75.92 | 75.92 | 75.92 | 75.92 | 75.92 | 75.92 | 75.92 | 75.92 | 75.92 | 75.92 | 75.92
ΔP Motor House - Evap | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.6217 | 7.7222 | 7.579 | 7.4999 | #N/A
Bearing Temp | 158.54 | 158.54 | 158.54 | 158.54 | 158.54 | 158.54 | 158.54 | 158.54 | 158.54 | 158.54 | 158.54
Oil Temp @ Sump | 140.36 | 140.36 | 140.36 | 140.36 | 140.36 | 140.36 | 140.36 | 140.36 | 140.36 | 140.36 | 140.36
Oil Reclaim Static Press. | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50.8787 | 50.9576 | 51.206 | 51.1134 | 51.2183
ΔP Oil DP | 40.4363 | 40.0012 | 39.6531 | 40.7989 | 41.0454 | 39.8706 | 42.8004 | 42.0752 | 42.4233 | 40.5088 | 40.7844
Electrical Parameters
Frequency | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2
Current (A) | 66.0563 | 69.0346 | 70.6297 | 72.4477 | 73.8965 | 77.1591 | 61.5613 | 61.5816 | 60.408 | 60.514 | 74.3607
Current (B) | 66.0937 | 69.126 | 70.5863 | 72.492 | 74.0358 | 77.6848 | 61.4309 | 61.2518 | 60.1495 | 60.3889 | 74.0539
Current(C) | 64.6454 | 67.7363 | 69.0845 | 71.1023 | 72.3785 | 75.972 | 60.2171 | 60.0044 | 58.9427 | 59.1755 | 72.5989
Voltage(A) | 9.3158 | 9.3223 | 9.3405 | 9.336 | 9.3788 | 9.1312 | 9.5557 | 9.8132 | 9.7004 | 9.685 | 9.6725
Voltage(B) | 9.4691 | 9.4695 | 9.4862 | 9.483 | 9.5242 | 9.3142 | 9.7141 | 9.9795 | 9.9138 | 9.8808 | 9.8227
Voltage(C) | 9.3326 | 9.324 | 9.3435 | 9.3388 | 9.3748 | 9.1533 | 9.5241 | 9.7775 | 9.663 | 9.6495 | 9.6721
Measured Power Factor | 0.9 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.84 | 0.9 | 0.91
Calculated Power Factor | 0.90887 | 0.9097 | 0.90982 | 0.90958 | 0.90849 | 0.91021 | 0.9051 | 0.90219 | 0.90228 | 0.90318 | 0.90826
PF Tolerance | -0.976% | 0.03271% | 0.0199% | 0.04584% | 0.1662% | -0.02281% | 0.5412% | 0.8658% | -6.903% | -0.3518% | 0.1919%
Aero Data
ETA | 0.75379 | 0.74986 | 0.75128 | 0.75161 | 0.75936 | 0.73903 | 0.8234 | #NAME? | #NAME? | #NAME? | 0.81695
LCO | 1.085% | 1.095% | 1.05% | 1.007% | 0.7287% | 1.105% | 0.776% | #NAME? | #NAME? | #NAME? | 1.566%
Full stage (vessel to flange)
FF | 7.8449 | 8.1966 | 8.3702 | 8.5724 | 8.8319 | 8.7795 | #VALUE! | #NAME? | #NAME? | #NAME? | 9.5102
HF | 24.5607 | 24.6335 | 24.8364 | 24.9727 | 25.3458 | 25.3501 | #VALUE! | #NAME? | #NAME? | #NAME? | 30.9363
EFF | 0.75379 | 0.74986 | 0.75128 | 0.75161 | 0.75936 | 0.73903 | #VALUE! | #NAME? | #NAME? | #NAME? | 0.81695
1st Stage (vessel to RC exit)
FF | 7.8449 | 8.1966 | 8.3702 | 8.5724 | 8.8319 | 8.7795 | #VALUE! | #NAME? | #NAME? | #NAME? | 9.5102
HF | 12.4306 | 13.0709 | 13.4382 | 13.8001 | 14.3545 | 14.6708 | #VALUE! | #NAME? | #NAME? | #NAME? | 16.1173
EFF | 0.74021 | 0.73648 | 0.73789 | 0.73834 | 0.74608 | 0.72628 | #VALUE! | #NAME? | #NAME? | #NAME? | 0.80189
2nd Stage (RC exit to flange)
FF | 5.8265 | 5.9406 | 5.9899 | 6.0538 | 6.1204 | 6.0003 | #VALUE! | #NAME? | #NAME? | #NAME? | 6.3878
HF | 12.0893 | 11.5206 | 11.359 | 11.1359 | 10.9627 | 10.6287 | #VALUE! | #NAME? | #NAME? | #NAME? | 14.7458
EFF | 0.74021 | 0.73648 | 0.73789 | 0.73834 | 0.74608 | 0.72628 | #VALUE! | #NAME? | #NAME? | #NAME? | 0.80189
Orifice Ent. Temp. | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.7921e+38 | 1.759e+38 | 1.7921e+38 | 1.7921e+38 | 1.059e+38
Flasc Exit Static Press. | 130.2358 | 130.3766 | 130.8814 | 131.2758 | 131.6068 | 131.2216 | 131.1282 | 130.9534 | 130.3353 | 130.2535 | 130.8362
m_suction | 5076.4213 | 5299.9023 | 5398.9837 | 5527.2708 | 5636.5711 | 5642.0884 | #VALUE! | #NAME? | #NAME? | #NAME? | 5009.8175
m_eco | 460.419 | 450.819 | 451.0926 | 448.5793 | 449.1724 | 414.8677 | #VALUE! | #NAME? | #NAME? | #NAME? | 561.3634
Condenser Level | Full W/ bubble | Full W/o bubble |  |  |  |  | 44.7583 | 45.0048 | 45.1148 | 44.9376
[7 empty] | 76.7755 | 76.8943 | 76.6532 | 76.8385
[7 empty] | 42.123 | 42.5171 | 42.7919 | 42.6687
[7 empty] | 86.857 | 87.6222 | 87.1913 | 87.3133
[7 empty] | 125.2534 | 125.4042 | 124.8194 | 124.7831
[8 empty] | 0.1466 | 0.1466 | 0.1466
|  |  | ρv^2 | Eyehole velocity ft/s | 1/1*Eyehole velocity ft/s
|  |  | 0 | 1.62 | 1.782
|  |  | 4400 | 1.532 | 1.532
|  |  | 1750 | 1.585 | 1.7435
|  |  | 4400 | 0 | 0