## 19XR6 FrB cooler Check
PARAMETER
INPUT |  |  | 注释 | 此Tool仅应用于19XR6+FrB cooler数据中心中温工况ETO订单中，采用XR7 7S经济器和7F高侧浮球阀 Igonre Carryover的选型进行校核。 首台订单应用必须进行5天性能测试。
Refrigerant |  | R134a |  | Comments:
Chiller Capacity | tons | 2800 | #此值根据E-Cat报告进行输入 |  | 该区域值来自E-Cat报告（Ignore LCO)
Cooler Size |  | B6H | #此值根据E-Cat报告进行选择 | 7S | 19XR7 经济器浮球阀代号
Cooler Passes |  | 2 | #此值根据E-Cat报告进行选择 | OK | E-Cat 选型符合EDR的限制
Cooler Nozzle Arrangement |  | Drive End | #此值根据E-Cat报告进行选择 | NO | E-Cat 选型不符合EDR的限制
Cooler Entering Temperature | F | 71.6 | #此值根据E-Cat报告进行输入 | Pass | E-Cat 选型工况同时满足EDR中经济器和蒸发器的限制
Cooler Saturation Temperature(Tsat,clr) | F | 58.4 | #此值根据E-Cat报告进行输入 | Failed | E-Cat 选型工况不满足EDR中经济器或蒸发器的限制
Cooler Leaving Temperature | F | 59 | #此值根据E-Cat报告进行输入
Condenser Saturation Temperature | F | 106.7 | #此值根据E-Cat报告进行输入
Flasc SaturationTemperature | F | 100.2 | #此值根据E-Cat报告进行输入
ETO Economizer Float Valve Size |  | 7S | #此值根据ETO选型进行选择,代号含义见Comments
Economizer Saturation Temperature(Tsat,eco) | F | 81.99 | #此值根据E-Cat报告进行输入
Discharge Super Heat | R | 11.57 | #此值根据E-Cat报告进行输入
Evaporator LTD | R | 0.6 | #此值根据E-Cat报告进行输入
EDR Limit
Vapor Limit(EDR) | ft^3/min | #NAME? | #EDR中经济器气体体积流量限制值
Liquid Limit(EDR) | ft/s | #NAME? | #EDR中经济器眼睛口液体流速限制值
Cooler Limit Tons | tons | 3148.497
Check
Economizer Vapor Volume Flow Rate | ft^3/min | #NAME? | #E-Cat选型中，经济器气体体积流量
V_EyeHole.Liquid m1st | ft/s | #NAME? | #E-Cat选型中，经济器眼睛口液体流速
Economizer Vapor Volume Flow Rate | ft^3/min | #NAME? | #判断E-Cat选型中经济器的气体体积流量是否满足EDR限制
V_EyeHole.Liquid m1st | ft/s | #NAME? | #判断E-Cat选型中经济器的液体流速是否满足EDR限制
Cooler Limit check | tons | OK | #判断E-Cat选型中蒸发器的Limit Tons是否满足EDR限制
Result |  | #NAME? | #判断E-Cat选型中经济器和蒸发器的Limit Tons是否均满足EDR限制
结论: |  | #NAME?

## Category (hidden)
PASS | Cooler Nozzle Arrangement | Cooler Size | Cooler Length | ETO Economizer Float Valve Size | Tube No
1 | Drive End | B60 | 16 | 7S | 1280
2 | Compressor End | B61 |  |  | 1413
3 |  | B62 |  |  | 1540
|  | B65 |  |  | 1318
|  | B66 |  |  | 1448
|  | B67 |  |  | 1576
|  | B6A |  |  | 686
|  | B6B |  |  | 763
|  | B6C |  |  | 843
|  | B6F |  |  | 715
|  | B6G |  |  | 796
|  | B6H |  |  | 875

## 19XR6 Fr B_Evap (hidden)
Input_E-cat report
| Case Name |  | Case 1
自动链接 无需填写 | Chiller Capacity | Ton | 2800
| Cooler Size |  | B6H
| Cooler Length | ft | 16
| Cooler Passes |  | 2
| Cooler Nozzle Arrangement |  | Drive End
| Cooler Entering Temperature | F | 71.6
| Cooler Leaving Temperature | F | 59
| Cooler Saturation Temperature(Tsat,clr) | F | 58.4
| Economizer Saturation Temperature(Tsat,eco) | F | 81.99
| The cooler Temp rise | F | 12.6
Output_Cooler Limit Tons
| Baseline Capacity |  | 2510
| X1 |  | -2.0099e-09
| X2 |  | 1.123e-07
| X3 |  | 7.021e-05
| C1 |  | 6.5906e-05
| Y1 |  | 6.8044e-08
| Y2 |  | -4.9788e-05
| Y3 |  | 0.012676
| C2 |  | 0.0090513
| Z1 |  | -3.5061e-06
| Z2 |  | -0.0018123
| Z3 |  | 0.64005
| C3 |  | 0.46789
| Lift Multiplier |  | 1.2213
| A1 |  | 1.3156e-05
| A2 |  | -0.00090031
| A3 |  | 0.025717
| A4 |  | 0.8197
| Rise Multiplier |  | 1.0271
| Cooler Limit Tons | Ton | 3148.497
Pass or not
Compressor End
Drive End

## 19XR7_Econ (hidden)
R7 Economizer
| PARAMETER |  | Cooler:14/20 Condenser: 32/37
INPUT
自动链接 无需填写 | Refrigerant |  | R134a
| Capacity | tons | 2800
| Flasc SaturationTemperature | F | 100.2
| Economizer Saturation Temperature | F | 81.99
| Cooler Saturation Temperature | F | 58.4
| Condenser Saturation Temperature | F | 106.7
| Discharge Super Heat | R | 11.57
| Evaporator LTD | R | 0.6
| System Lift | R | 48.3
Constant
| Acceleration of Gravity | ft/sec^2 | 32.174
OUTPUT
| Cooler Saturation vapor Enthalpy h | Btu/lbm | #NAME?
| Cooler SaturationLiquid Enthalpy h | Btu/lbm | #NAME?
| Flasc Saturation Liquid Enthalpy h5 | Btu/lbm | #NAME?
| Economizer Saturation Liquid Enthalpy h6 | Btu/lbm | #NAME?
| Economizer Saturation Vapor Enthalpy h7 | Btu/lbm | #NAME?
| Economizer Vapor quality |  | #NAME?
| Refrigerator Dryness |  | #NAME?
| Economizer Saturation Liquid Density | lbm/ft^3 | #NAME?
| Economizer Saturation Vapor Density | lbm/ft^3 | #NAME?
| Economizer Mixture Density | lbm/ft^3 | #NAME?
| 1st stage Mass Flow Rate | lb/min | #NAME?
| Econ Vapor Mass Flow Rate | lb/min | #NAME?
| Econ Liquid Mass Flow Rate | lb/min | #NAME?
| Economizer Vapor Volume Flow Rate | ft^3/min | #NAME?
| Economizer Liquid Volume Flow Rate | ft^3/min | #NAME?
Assume
| Shell ID | in
| Shell Length | in
| d_ 2nd stg Vapor | in
| d_ Econ. Liquid | in
| A_EyeHole | ft^2 | 1.24
Calculation
| A_Econ Shell_H | ft^2 | 0
| A_Econ Shell_V | ft^2 | 10.96
| A_ 2nd stg Vapor | ft^2 | 0
| A_ Econ. Liquid | ft^2 | 0
Check
| V_ 2nd stg Vapor | ft/s | #NAME?
| V_ Econ. Liquid | ft/s | #NAME?
| V_EyeHole.Liquid m1st | ft/s | #NAME?
| V_Liquid_Econ_H | ft/s | #NAME?
| V_Vapor_Econ_H | ft/s | #NAME?
| V_Vapor_Econ_V | ft/s | #NAME?
| ρv^2 (Vapor)<*** |  | #NAME?
| Lliquid carry over | %
| Vapor Limit(EDR) | ft^3/min | #NAME?
| Liquid Limit(EDR) | ft/s | #NAME?

## EDR Database-Fr B cooler (hidden)
Cooler Frame | Baseline Capacity (Ton) | [5 empty] | Cooler Length
| Compressor End |  |  | Drive End
| 1 pass | 2 pass | 3 pass | 1 pass | 2 pass | 3 pass |  | 2 | pass | 3 | pass
B60 | N/A | N/A | 2066 | N/A | N/A | 2597 | 16
B61 | N/A | N/A | 1953 | N/A | N/A | 2503 | 16
B62 | N/A | N/A | 1843 | N/A | N/A | 2400 | 16
B65 | 1918 | 2066 | N/A | 2982 | 2695 | N/A | 16
B66 | 1821 | 1953 | N/A | 2903 | 2606 | N/A | 16
B67 | 1733 | 1843 | N/A | 2810 | 2510 | N/A | 16
B6A | N/A | N/A | 2283 | N/A | N/A | 2645 | 16
B6B | N/A | N/A | 2173 | N/A | N/A | 2552 | 16
B6C | N/A | N/A | 2061 | N/A | N/A | 2452 | 16
B6F | 2089 | 2283 | N/A | 2858 | 2693 | N/A | 16
B6G | 1996 | 2173 | N/A | 2780 | 2606 | N/A | 16
B6H | 1898 | 2061 | N/A | 2689 | 2510 | N/A | 16
Cooler Length / ft | Compressor End | Drive End
| 16 | 16
A1 | -1.6509e-06 | 1.3156e-05
A2 | 0.00021082 | -0.00090031
A3 | -0.0091856 | 0.025717
A4 | 1.0724 | 0.8197
Lift Multiplier |  | Compressor End | Drive End
C1 | X1 | -5.9396e-10 | -2.0099e-09
| X2 | -1.3615e-07 | 1.123e-07
| X3 | 8.9202e-05 | 7.021e-05
C2 | Y1 | -2.5359e-08 | 6.8044e-08
| Y2 | -4.0841e-05 | -4.9788e-05
| Y3 | 0.012396 | 0.012676
C3 | Z1 | -2.0477e-06 | -3.5061e-06
| Z2 | -0.0021093 | -0.0018123
| Z3 | 0.64294 | 0.64005