## 19XRC Low Lift Eco&Cooler Check
PARAMETER
INPUT |  |  | 注释 | 此Tool仅应用于19XRC数据中心中温工况ETO订单中，采用XRC Fr 7经济器 Igonre Carryover的选型进行校核。 首台订单应用必须进行5天性能测试。
Refrigerant |  | R134a |  | Comments:
Chiller Capacity | tons | 1300 | #此值根据E-Cat报告进行输入 |  | 该区域值来自E-Cat报告（Ignore LCO)
Cooler Size |  | 70 | #此值根据E-Cat报告进行选择 | D | 19XRC 经济器浮球阀代号
Cooler Passes |  | 2 | #此值根据E-Cat报告进行选择 | OK | E-Cat 选型符合EDR的限制
Cooler Nozzle Arrangement |  | Drive End | #此值根据E-Cat报告进行选择 | NO | E-Cat 选型不符合EDR的限制,也不满足ETO特殊设计
Cooler Entering Temperature | F | 71.6 | #此值根据E-Cat报告进行输入 | Pass | E-Cat 选型工况同时满足EDR中经济器和蒸发器的限制
Cooler Saturation Temperature(Tsat,clr) | F | 58.4 | #此值根据E-Cat报告进行输入 | Failed | E-Cat 选型工况不满足EDR中经济器和蒸发器的限制中的任一项
Cooler Leaving Temperature | F | 59 | #此值根据E-Cat报告进行输入
Condenser Saturation Temperature | F | 106.7 | #此值根据E-Cat报告进行输入
Flasc SaturationTemperature | F | 100.2 | #此值根据E-Cat报告进行输入
ETO Economizer Float Valve Size |  | D | #此值根据ETO选型进行选择,代号含义见Comments
Economizer Saturation Temperature(Tsat,eco) | F | 81.99 | #此值根据E-Cat报告进行输入
Discharge Super Heat | R | 11.57 | #此值根据E-Cat报告进行输入
Evaporator LTD | R | 0.6 | #此值根据E-Cat报告进行输入
EDR Limit
Vapor Limit(EDR) | ft^3/min | 250 | #EDR中经济器气体体积流量限制值
Liquid Limit(EDR) | ft/s | #NAME? | #EDR中经济器眼睛口液体流速限制值
Liquid Limit(ETO Economizer) | ft/s | #NAME? | #ETO中经济器眼睛口液体流速限制值
Cooler Limit Tons | tons | 1746.2987
Check
Economizer Vapor Volume Flow Rate | ft^3/min | #NAME? | #E-Cat选型中，经济器气体体积流量
V_EyeHole.Liquid m1st | ft/s | #NAME? | #E-Cat选型中，经济器眼睛口液体流速
Economizer Vapor Volume Flow Rate | ft^3/min | #NAME? | #判断E-Cat选型中经济器的气体体积流量是否满足EDR限制
V_EyeHole.Liquid m1st | ft/s | #NAME? | #判断E-Cat选型中经济器的液体流速是否满足EDR或ETO限制
Cooler Limit check | tons | OK | #判断E-Cat选型中蒸发器的Limit Tons是否满足EDR限制
Result |  | #NAME? | #判断E-Cat选型中经济器和蒸发器的Limit Tons是否均满足EDR限制
结论: |  | #NAME?

## Category
PASS | Cooler Nozzle Arrangement | Cooler Size | Cooler Length | ETO Economizer Float Valve Size
1 | Drive End | 70 | 12 | D
2 | Compressor End | 71 | 14
3 |  | 72 | 16
73
74
75
76
77
78
79
7K
7L
7M
7P
7Q
7R
7T
7U
7V
7X
7Y
7Z

## 19XRC_Evap
| Input_E-cat report |  |  | 只能单独一列检查
| Case Name |  | Case 1
自动链接 无需填写 | Chiller Capacity | Ton | 1300
| Cooler Size |  | 70
| Cooler Length | ft | 14
| Cooler Passes |  | 2
| Cooler Nozzle Arrangement |  | Drive End
| Cooler Entering Temperature | F | 71.6
| Cooler Leaving Temperature | F | 59
| Cooler Saturation Temperature(Tsat,clr) | F | 58.4
| Economizer Saturation Temperature(Tsat,eco) | F | 81.99
| The cooler Temp rise | F | 12.6
Output_Cooler Limit Tons
| Baseline Capacity |  | 1321
| X1 |  | -2.1355e-09
| X2 |  | 1.1951e-07
| X3 |  | 7.4529e-05
| C1 |  | 6.9972e-05
| Y1 |  | 7.2381e-08
| Y2 |  | -5.2881e-05
| Y3 |  | 0.013459
| C2 |  | 0.0096099
| Z1 |  | -3.7262e-06
| Z2 |  | -0.0019233
| Z3 |  | 0.67948
| C3 |  | 0.49674
| Lift Multiplier |  | 1.2966
| A1 |  | -6.1431e-05
| A2 |  | 0.0086862
| A3 |  | 0.91986
| Rise Multiplier |  | 1.0196
| Cooler Limit Tons | Ton | 1746.2987
Pass or not
Compressor End
Drive End

## 19XRC_Econ
18inch Economizer
| PARAMETER |  | Cooler:14/20 Condenser: 32/37
INPUT
自动链接 无需填写 | Refrigerant |  | R134a
| Capacity | tons | 1300
| Flasc SaturationTemperature | F | 100.2
| Economizer Saturation Temperature | F | 81.99
| Cooler Saturation Temperature | F | 58.4
| Condenser Saturation Temperature | F | 106.7
| Discharge Super Heat | R | 11.57
| Evaporator LTD | R | 0.6
| System Lift | R | 48.3
Constant
| Acceleration of Gravity | ft/sec^2 | 32.174
OUTPUT
| Cooler Saturation vapor Enthalpy h | Btu/lbm | #NAME?
| Cooler SaturationLiquid Enthalpy h | Btu/lbm | #NAME?
| Flasc Saturation Liquid Enthalpy h5 | Btu/lbm | #NAME?
| Economizer Saturation Liquid Enthalpy h6 | Btu/lbm | #NAME?
| Economizer Saturation Vapor Enthalpy h7 | Btu/lbm | #NAME?
| Economizer Vapor quality |  | #NAME?
| Refrigerator Dryness |  | #NAME?
| Economizer Saturation Liquid Density | lbm/ft^3 | #NAME?
| Economizer Saturation Vapor Density | lbm/ft^3 | #NAME?
| Economizer Mixture Density | lbm/ft^3 | #NAME?
也可以用ECAT输出报告中的Suction Mass Flow | 1st stage Mass Flow Rate | lb/min | #NAME?
也可以用ECAT输出报告中的Suction Mass Flow与Discharge Mass Flow的差值 | Econ Vapor Mass Flow Rate | lb/min | #NAME?
| Econ Liquid Mass Flow Rate | lb/min | #NAME?
| Economizer Vapor Volume Flow Rate | ft^3/min | #NAME?
| Economizer Liquid Volume Flow Rate | ft^3/min | #NAME?
Assume
不同经济器的参数不同，ETO经济器可能修改 | Shell ID | in | 17.2126
| Shell Length | in | 47.4 | 58.4 | 47.4
| d_ 2nd stg Vapor | in | 4
| d_ Econ. Liquid | in | 4
| A_EyeHole | ft^2 | 0.435
Calculation
| A_Econ Shell_H | ft^2 | 1.6159
不同经济器的参数不同，ETO经济器可能修改 | A_Econ Shell_V | ft^2 | 5.45
| A_ 2nd stg Vapor | ft^2 | 0.087266
| A_ Econ. Liquid | ft^2 | 0.087266
| Check |  |  |  |  | XRC Standard Economizer limit curve
| V_ 2nd stg Vapor | ft/s | #NAME? |  |  | ρv^2 (Vapor) | Liquid Limit(EDR)
| V_ Econ. Liquid | ft/s | #NAME? |  |  | 0 | 1.87
| V_EyeHole.Liquid m1st | ft/s | #NAME? |  |  | 1500 | 1.87 | 0-1500 | y=1.87
| V_Liquid_Econ_H | ft/s | #NAME? |  |  | 3021 | 1.76 | 1500-3021 | y=1.87-(1.87-1.76)*(D52-1500)/(3021-1500)
| V_Vapor_Econ_H | ft/s | #NAME? |  |  | 8900 | 1.6 | 3021-8900 | y=1.76-(1.76-1.6)*(D52-3021)/(8900-3021)
| V_Vapor_Econ_V | ft/s | #NAME?
| ρv^2 (Vapor)<*** |  | #NAME?
| Lliquid carry over | % |  |  |  | 1400T ETO Economizer limit curve
| Vapor Limit(EDR) | ft^3/min | 250 |  |  | ρv^2 (Vapor) | Liquid Limit(EDR)
| Liquid Limit(EDR) | ft/s | #NAME? |  |  | 0 | 2.1
| Liquid Limit(ETO) | ft/s | #NAME? |  |  | 800 | 2.1 | 0-800 | y=2.1
[6 empty] | 1500 | 1.87 | 800-1500 | y=2.1-((2.1-1.87)/(1500-800))*(D52-800)
[6 empty] | 3021 | 1.76 | 1500-3021 | y=1.87-(1.87-1.76)*(D52-1500)/(3021-1500)
[6 empty] | 8900 | 1.6 | 3021-8900 | y=1.76-(1.76-1.6)*(D52-3021)/(8900-3021)

## EDR Database-XRC
Cooler Frame | Baseline Capacity (Ton) | [5 empty] | Cooler Length
| Compressor End |  |  | Drive End
| 1 pass | 2 pass | 3 pass | 1 pass | 2 pass | 3 pass
70 | 1165 | 1226 | 1225 | 1424 | 1321 | 1295 | 14
71 | 1092 | 1145 | 1145 | 1349 | 1250 | 1221 | 14
72 | 1018 | 1064 | 1064 | 1268 | 1174 | 1143 | 14
73 | N/A | N/A | 1064 | N/A | N/A | 1143 | 14
74 | 1018 | 1064 | N/A | 1268 | 1174 | N/A | 14
75 | 1408 | 1415 | 1401 | 1497 | 1450 | 1426 | 16
76 | 1327 | 1330 | 1315 | 1412 | 1367 | 1341 | 16
77 | 1243 | 1242 | 1226 | 1323 | 1279 | 1253 | 16
78 | N/A | N/A | 1226 | N/A | N/A | 1253 | 16
79 | 1243 | 1242 | N/A | 1323 | 1279 | N/A | 16
7K | N/A | N/A | 1423 | N/A | N/A | 1464 | 14
7L | N/A | N/A | 1362 | N/A | N/A | 1406 | 14
7M | N/A | N/A | 1298 | N/A | N/A | 1344 | 14
7P | 1355 | 1427 | N/A | 1569 | 1475 | N/A | 14
7Q | 1296 | 1366 | N/A | 1513 | 1419 | N/A | 14
7R | 1234 | 1301 | N/A | 1451 | 1359 | N/A | 14
7T | N/A | N/A | 1609 | N/A | N/A | 1625 | 16
7U | N/A | N/A | 1542 | N/A | N/A | 1558 | 16
7V | N/A | N/A | 1470 | N/A | N/A | 1487 | 16
7X | 1600 | 1619 | N/A | 1680 | 1637 | N/A | 16
7Y | 1535 | 1552 | N/A | 1614 | 1572 | N/A | 16
7Z | 1466 | 1481 | N/A | 1544 | 1503 | N/A | 16
Cooler Length / ft | Compressor End |  |  | Drive End
| 12 | 14 | 16 | 12 | 14 | 16
A1 | 0.00013734 | 2.2688e-05 | -3.7504e-05 | -7.1646e-05 | -6.1431e-05 | -8.7204e-05
A2 | -0.010517 | -0.0017183 | 0.003987 | 0.010838 | 0.0086862 | 0.0082889
A3 | 1.0897 | 1.0146 | 0.96392 | 0.89957 | 0.91986 | 0.92563
|  |  |  | Lift Multiplier | C1 |  |  | C2 |  |  | C3
[5 empty] | X1 | X2 | X3 | Y1 | Y2 | Y3 | Z1 | Z2 | Z3
|  |  |  | Compressor End | -6.3024e-10 | -1.4624e-07 | 9.5348*10^(-5) | -2.7298e-08 | -4.3609e-05 | 1.3245*10^(-2) | -2.1893e-06 | -0.0022537 | 6.8701*10^(-1)
|  |  |  | Drive End | -2.1355e-09 | 1.1951*10^(-7) | 7.4529*10^(-5) | 7.2381*10^(-8) | -5.2881e-05 | 1.3459*10^(-2) | -3.7262e-06 | -0.0019233 | 6.7948*10^(-1)
|  |  |  | Lift Multiplier | C1 X2: Compressor End; C1 X3: Drive End
|  |  |  | C1 | C1 X1: X1; C1 X2: -6.3024e-10; C1 X3: -2.1355e-09
[5 empty] | X2 | -1.4624e-07 | 1.1951e-07
[5 empty] | X3 | 9.5348e-05 | 7.4529e-05
|  |  |  | C2 | C1 X1: Y1; C1 X2: -2.7298e-08; C1 X3: 7.2381e-08
[5 empty] | Y2 | -4.3609e-05 | -5.2881e-05
[5 empty] | Y3 | 0.013245 | 0.013459
|  |  |  | C3 | C1 X1: Z1; C1 X2: -2.1893e-06; C1 X3: -3.7262e-06
[5 empty] | Z2 | -0.0022537 | -0.0019233
[5 empty] | Z3 | 0.68701 | 0.67948